{"text_format":"3","workbook":"xlsx","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"read":"whole","date_system":"1900"}

{"sheet":"Sheet1","index":0,"n_rows":22,"n_cols":12,"rows_kept":22,"merged":[[0,0,0,11],[1,0,1,11],[2,0,2,11],[3,0,4,0],[3,1,4,1],[3,2,4,2],[3,3,4,3],[3,4,4,4],[3,5,4,5],[3,6,4,6],[3,7,4,7],[3,8,4,8],[3,9,4,9],[3,10,3,11],[5,0,12,0],[5,1,19,1],[5,2,5,7],[5,10,12,10],[5,11,12,11],[6,3,6,4],[6,5,6,6],[8,3,8,5],[10,3,10,6],[11,3,11,6],[13,0,19,0],[13,2,13,7],[13,10,19,10],[13,11,19,11],[20,0,20,11],[21,0,21,11]]}
["公开询价报价表"]
["单位： 莆田市绶溪建设开发有限公司                   询价时间：2024年12月6日"]
["询  价  情  况"]
["序号","被询价单位及\n联系人、联系电话","物资名称","型号\nType","流量\nCapacity\n(m³/h)","扬程\nHead\n（m）","功率\nPower\n（Kw）","备注","数量","单位","金额（元，含税）"]
[{"$nulls":10},"单价      ","总价     "]
[1,null,"灌溉给水控制主机含配套水泵一体化（厂家可自行深化）",{"$nulls":5},1,"套"]
[null,null,"不锈钢泵房","304不锈钢水箱4500*5000*2000H，(内部隔间尺寸3000*2000*2000H用于放置给水设备)",null,"盖  板：1.0mm\n侧板二：1.2mm\n侧板一：1.5mm\n底  板：1.5mm",null,"含底座，含阀门管路等，含水箱进出水阀门，泄水阀，泵房内管道、电线电缆，不含土建。",1,"台"]
[null,null,"多级离心泵","ZLDF20-10","20m³/h",118,11,"过流部件304材质",2,"台"]
[null,null,"控制系统","一控二智能变频供水系统/含PLC编程模块/+潜污泵11KW直启一用一备",null,null,11,"专业供水软件",1,"台"]
[null,null,"气压罐","100L","/","/","/","碳钢材质、内有胶囊",1,"台"]
[null,null,"给水设备附件","含槽钢底座，阀门，水泵口径DN50*2台不锈钢管路机组等",{"$nulls":3},"过流部件304材质，含与水箱连接管道阀门。",1,"台"]
[null,null,"自动反冲洗过滤器","进出口DN150，流量100m3/h,过滤直径80目",{"$nulls":3},"自清洗网式过滤器（电刷式），碳钢材质，DN150，含进出管道及阀门",1,"台"]
[null,null,"潜污泵","100WQ80-25-11","80m³/h",25,11,"铸铁材质/2900转",2,"台"]
[2,null,"生活给水供水设备（厂家可自行深化）",{"$nulls":5},1,"套"]
[null,null,"多级离心泵","ZLDF20-5","20m³/h",58,5.5,"过流部件304材质",3,"台"]
[null,null,"变频控制柜","一控三/智能变频供水系统/含PLC编程模块/可自动轮泵、自动加减泵",null,null,5.5,"专业供水软件",1,"台"]
[null,null,"气压罐","100L","/","/","/","碳钢材质、内有胶囊",1,"台"]
[null,null,"附件","含槽钢底座，阀门，水泵口径DN50*3台不锈钢管路机组等（进水总管DN100、出水总管DN150）",{"$nulls":3},"过流部件304材质含与水箱连接管道阀门。",1,"台"]
[null,null,"不锈钢水箱（304#材质）","4*4*2（m）","水箱容积32m³","盖  板：1.0mm\n侧板二：1.2mm\n侧板一：1.5mm\n底  板：1.5mm",null,"生活水箱/含镀锌槽钢底座，含水箱出水阀门，泄水阀，泵房内管道、电线电缆桥架，不含土建。",1,"台"]
[null,null,"给水设备附件","泵房内供水设备及控制柜的就位安装，管道阀门连接，电线电缆桥架，支托架，",{"$nulls":4},1,"台"]
["合计：         元（含税）"]
["备注：报价应包含税金（增值税专用发票）、运费等一切费用"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0}